Hycrete, Inc.

14 Spielman Road

Fairfield, NJ 07004

Office: (201) 386-8110

Fax: (201) 386-8155

Website:	   www.hycrete.com

SECTION 03 05 11

HYDROPHOBIC CONCRETE

OUTLINE SPECIFICATION

This outline specification is available for insertion into your concrete specification. You should ensure that the concrete design and construction quality requirements in your concrete specification meet the long-form version of this specification, available as a separate document, in order that

Hycrete Endure WP (Formerly Hycrete W1000) hydrophobic concrete admixture can meet performance requirements.

Please contact Hycrete to ensure that this product is suitable for your project.

For information on Hycrete Endure WP, including performance and applications, please contact Hycrete, Inc. or visit www.hycrete.com.

For best results, display hidden notes to specifier – click on ¶.

This specification is provided to coordinate the use of Hycrete W1000 within the project, installed as part or all of the concrete works. The hydrophobic concrete admixture is required to be mixed in with the concrete batch prior to concrete placement.

This section includes products manufactured by Hycrete, Inc.:

Hycrete, Inc.

462 Barell Avenue

Carlstadt, NJ 07072

(201) 386 8110

www.hycrete.com

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

Always check the application and design details with the Manufacturer before designing, bidding, and construction.

PART 1 GENERAL

  - SUMMARY

  - This section specifies concrete with Hydrophobic Concrete Admixture as indicated on the project drawings for the following:

Revise list below to suit Project.

    - Footings

    - Foundation walls

    - Slabs-on-grade

    - Suspended slabs

    - Water tanks

    - Tunnels

    - (Other-specify)

  - QUALITY ASSURANCE

  - Hydrophobic Concrete Admixture Manufacturer Qualifications: Hydrophobic Concrete Admixture Manufacturer will have a minimum of 5 years of experience on projects of similar scope.

  - PRE-INSTALLATION CONFERENCE

  - Attendance:  Contractor, installer, owner, architect, structural engineer, civil engineer, Hydrophobic Concrete Admixture Manufacturer representative, batch plant representative, and those requested to attend.

  - Meeting Time:  Minimum of 3 weeks prior to the beginning of the work of this Section and work of related Sections affecting the work of this Section.

  - Location:  Project site.

  - Review procedures for conducting work of this Section, including:

    - Review of mix design and mix test results.

    - Mixing procedure.

    - Conditions for acceptance of concrete at project site.

    - Placement procedures.

    - Finishing options and procedures.

    - Curing and crack control procedures.

    - Testing for acceptable moisture emissions, alkalinity pH levels, and relative humidity of concrete slab prior to installation of finish flooring.

    - Affect of the above on the project schedule.

  - DELIVERY, STORAGE, AND HANDLING

  - Conform to provisions of the Section 01 65 10 and the Hydrophobic Concrete Admixture Manufacturer instructions.

  - Mixing and Delivery:  Conform to ASTM C94.

  - Sampling at Delivery:  Conform to ASTM C172.  Cure 4-inch by 8-inch cylinders to provisions of ASTM C31 and compression test compressive strength of cylinders to ASTM C39.

  - Batch Tickets:  Conform to ASTM C94 Option A or C.  Accompany each load, fully executed, and signed.  Log in with inspector at time of entry.  Conform to Source Quality Control requirements specified by this Section.

    - Include water content and water withheld at batch plant.

    - Indicate time to nearest minute that batch was dispatched from plant, when it arrived at site, and when unloading began and was finished.

    - Indicate ambient air temperature and concrete internal temperature at time of arrival.

    - Make written record of water and other additives added to design mix, and the amount of concrete in the truck at the time of addition, after the mix truck left the batch plant.

  - Reject concrete that has reached internal temperature of 89 degrees Fahrenheit or above and when temperature has risen 5 degrees in 10 minutes, indicating concrete is setting up prior to discharge.

  - Store products in accordance with ACI 301.  Do not use admixtures that have been in storage at project site for more than 12 months or which have been subjected to freezing, except as accepted by the Hydrophobic Concrete Admixture Manufacturer and by the structural engineer based on test results.

PART 2 PRODUCTS

  - HYDROPHOBIC CONCRETE ADMIXTURE

  - Product generic name: Water-Based Hydrophobic Concrete Admixture.

  - Product name: Hycrete Endure WP (Formerly Hycrete W1000), as manufactured by Hycrete, Inc., 14 Spielman Road, Fairfield, New Jersey, 07004, telephone (201) 386-8110, website www.hycrete.com.

  - Physical properties

    - Admixture to meet or exceed British Standards Institute (BSI) 1881-122 testing to performance of <1% water absorption.

Verify the warranty type and period with Hydrophobic Concrete Admixture Manufacturer.  Do not specify warranty period and conditions that manufacturer will not honor.

  - MIXES

  - The concrete ready mix supplier must contact the Hydrophobic Concrete Admixture Manufacturer before designing and testing any new mix designs, to receive guidance on achieving proper water absorption characteristics. The concrete ready mix supplier must also report the test results to the Hydrophobic Concrete Admixture Manufacturer. All values must be within the specification limits.

    - All concrete materials used for testing must be same as concrete materials used for construction.

    - Test result requirements for Hydrophobic Concrete in addition to engineer’s performance requirements:  Corrected 30 minute water absorption, age at test 7 days (BS 1881-122):  Not greater than 1.0%

  - Waterproofing System:  All concrete in the locations listed in section 1.01 will be waterproofed by the addition of Hydrophobic Concrete Admixture and additional ingredients including:

    - Hydrophobic Concrete Admixture at the rate of one U.S. gallon per cubic yard of concrete (5 liters per cubic meter).

    - Superplasticizer at the manufacturer’s recommended rate and appropriate for the placement requirements of the project.

  - Water-Cement Ratio:  0.42 maximum. Water content of Hydrophobic Concrete Admixture and other admixtures to be included in the water-to-cementitious ratio.

  - SOURCE QUALITY CONTROL

  - Verification of Performance:  Provide ready-mixed concrete from a concrete supplier approved by the Hydrophobic Concrete Admixture Manufacturer and authorized to dispense the Hydrophobic Concrete Admixture Manufacturer’s waterproofing materials.

PART 3 EXECUTION

  - MANUFACTURER’S INSTRUCTIONS

  - Comply with the Hydrophobic Concrete Admixture Manufacturer’s instructions and recommendations.

  - EXAMINATION

  - Site verification of conditions:

    - Verify that site conditions are acceptable for placement of waterproofed concrete.

    - Do not proceed with concrete placement until conditions unacceptable to the Hydrophobic Concrete Admixture Manufacturer are corrected.

  - Suitable Condition of Reinforcing Steel:

    - At the time concrete is placed, reinforcement shall be free from mud, oil, or other nonmetallic coatings that decrease bond. Epoxy-coating of steel reinforcement in accordance with standards shall be permitted.

    - Except for prestressing steel, steel reinforcement with rust, mill scale, or a combination of both shall be considered satisfactory, provided the minimum dimensions (including height of deformations) and weight of a hand-wire-brushed test specimen comply with ASTM A 615, ASTM A 706, ASTM A 996.

  - INSTALLATION

  - Waterstops and groutable hose waterstop system components:  Install in accordance with Hydrophobic Concrete Admixture Manufacturer’s recommendations.

    - Bentonite waterstops:

      - Shall be placed at all cold joints and penetrations

- Preparation:

  - Brush off all dust and debris and apply a coat of primer or spray adhesive to the area where the waterstop is to be placed on the standing structural member.

  - Using moderate hand pressure press a continuous bead of waterstop firmly into position on the standing structure. Check to be certain that the waterstop has bonded to the primed area.

  - For proper joining, cut ends with sharp tool at 45 degree angle, and then place ends over one another

  - Peel the protective backing from the exposed side of the waterstop. Knead the overlapped ends together to form continuous, uninterrupted gasket.

  - For shotcrete applications, in addition to the instructions above, utilize masonry nails to hold the waterstop in place.on the concrete. Masonry nails should be spaced approximately 12 inches apart. Waterstop must be glued and tied with the use of tie wires to all penetrations.

- Bentonite waterstops must not be installed more than 2 days prior to concrete placement. After installation of waterstops, cover the waterstop with a plastic sheet to protect from weather damage.

- Bentonite waterstops shall be dry and not activated when concrete is placed. If the waterstops have been water damaged they shall be replaced before the concrete is placed.

    - Other waterstops and groutable hose waterstop systems:

      - Shall be placed as on drawings.

  - Additional Reinforcement at Re-entrant Angles

    - Where re-entrant angles occur, three #4 or #5 bars spaced at 3 inches OC at least 3 feet long must be placed top and bottom at 90 degrees across all the angles.

  - Concrete:  Place, consolidate, and cure concrete in accordance with ACI 301, ACI 306, ACI 308, and ACI 309.

  - PROTECTION

  - Protect installed work from damage due to subsequent construction activity on the site.

    - Apply evaporation reducer (ACI 308) on flatwork immediately after finishing, as needed to maintain a film of water on the surface of the finished concrete until the final curing is applied, anytime the evaporation rate exceeds 0.10 lbs/ft2/hr.

    - Apply curing compound immediately to finished or stripped surfaces. A wax- or resin-based curing compound should be used if there is no subsequent finish on the structure. If there is a subsequent finish, a water-based curing compound should be used.

END OF SECTION